## Data
PLS-Pole XML File Description | C:\K2_Projects\Sample PLS-Pole Files\Sample Input File.xml
PLS-Pole XML File Version | 1
Project Name | a-frame
Project Path | C:\pls\spole\test a-frame.pol
Project Title | test
Project Notes | SWITCH TOWER
File Creation Date | 2005-07-25
Registered User Name | test
User Name | test
Program Version | 7.3
Load Case type | Vector
Number of Load Cases | 6
Number of Poles | 12
Number of Pole Property Sets | 2
Number of Tubular Davit Arms | 0
Number of Tubular Davit Property Sets | 0
Number of Tubular Cross Arms | 3
Number of Tubular Cross Arm Property Sets | 1
Number of Joints Defined | 16
Number of Baseplates Defined | 0
Number of Equipment Property Sets | 0
Number of Pieces of Equipment defined | 0
Steel Pole Data
| Pole | Property | Tip | Base | Base X | Base Y | Base Z | Inclin | Inclin | Base
| Name | Set Name | Joint | Joint | Coord. | Coord. | Coord. | About X | About Y | Connection
[5 empty] | (ft) | (ft) | (ft) | (deg) | (deg)
| PKL | 24920 PEAK | TOPX | TOPX | 0 | 0 | 0 | 0 | 0
| PKR | 24920 PEAK | TOPP | TOPP | 0 | 0 | 0 | 0 | 0
| LLF | 24920 LEG | CNTX | CNTX | 0 | 0 | 0 | 0 | 0
| LLB | 24920 LEG | CNTX | CNTX | 0 | 0 | 0 | 0 | 0
| RLF | 24920 LEG | CNTP | CNTP | 0 | 0 | 0 | 0 | 0
| RLB | 24920 LEG | CNTP | CNTP | 0 | 0 | 0 | 0 | 0
| PKRR | 24920 PEAK | TOPRP | TOPRP | 0 | 0 | 0 | 0 | 0
| RRLF | 24920 LEG | CNTRP | CNTRP | 0 | 0 | 0 | 0 | 0
| RRLB | 24920 LEG | CNTRP | CNTRP | 0 | 0 | 0 | 0 | 0
| PKLL | 24920 PEAK | TOPLP | TOPLP | 0 | 0 | 0 | 0 | 0
| LLLF | 24920 LEG | CNTLP | CNTLP | 0 | 0 | 0 | 0 | 0
| LLLB | 24920 LEG | CNTLP | CNTLP | 0 | 0 | 0 | 0 | 0
Steel Pole Property Data
| Property | No. of | Pole | Default | Pole | Pole | Tip | Base | Pole | Mod. of | Weight | Has
| Name | Tubes | Length | Embed. | Shape | Shape | Dia. | Dia. | Taper | Elast ovr | Dens Ovr | Baseplate?
|  |  | (ft) | (ft) |  | Base | (in) | (in) |  | (ksi) | (psf)
| 24920 PEAK | 1 | 18 | 0 | 12F |  | 12 | 16 | 0 | 29000 | 0.2836 | FALSE
| 24920 LEG | 1 | 52.2 | 0 | 12F |  | 16 | 0 | 0.1 | 29000 | 0.2836 | FALSE
Tube Data
| Property | Tube | Tube | Tube | Lap | Yield | Calc. | Tube | Top | Bot | 1.5 Dia | Lap | Mom Cap
| Name | Number | Length | Thick. | Length | Stress | Taper | Weight | Dia. | Dia. | Lap Len | Gap | Ovr
|  |  | (ft) | (in) | (ft) | (ksi) | (in/ft) | (lbf) | (in) | (in) | (ft) | (in) | (ft-k)
| 24920 PEAK | 1 | 18 | 0.1875 | 0 | 65 | 0.2222 | 510 | 12 | 16 | 0 | 0 | 0
| 24920 LEG | 1 | 52.2 | 0.1875 | 0 | 65 | 0.1 | 1973 | 16 | 21.22 | 0 | 0 | 0
Tubular Cross Arm Data
| Cross Arm |  | Property | [5 empty] | Number Of |  | Number Of
| Name |  | Set Name |  | Azimuth |  | Slope |  | Attachments |  | Connections
[5 empty] | (deg) |  | (deg)
| ARM1 |  | 24920 A-FR XARM |  | 0 |  | 0 |  | 0 |  | 8
| ARM2 |  | 24920 A-FR XARM |  | 0 |  | 0 |  | 0 |  | 8
| ARM3 |  | 24920 A-FR XARM |  | 0 |  | 0 |  | 0 |  | 8
Tubular Cross Arm Property Data
| Property |  | Steel | Wall | Section | Arm | Mod Of | Yield | # Geometry | Weight | Strength
| Name |  | Shape | Thick | Dia. | Length | Elast | Stress | Points | Dens Ovr | Check
|  |  |  | (in) | (in) | (ft) | (ksi) | (ksi) |  | (pcf) | Type
| 24920 A-FR XARM |  | 12F | 0.25 | 30 | 58 | 29000 | 65 | 6 | 0 | Calculated
Joint Support Reactions By Load Case
| Load |  | Joint | Long. (X) | Trans. (Y) | Vert. (Z) | Trans (X) | Long. (Y) | Vert. (Z)
| Case |  | Label | Force | Force | Force | Moment | Moment | Moment
| NESC LIGHT |  | TOPP | -22.79 | -2.68 | 81.28 | 73.35 | 23.6 | 22.98
| NESC LIGHT |  | CNTP | -10.34 | -3.79 | 39.99 | 92.8 | 25.8 | 20.78
| NESC LIGHT |  | BASEP | -9.51 | -2.14 | 37.23 | 56.9 | 26 | 21.95
| NESC LIGHT |  | TOPRP | -23.22 | -3.11 | 82.66 | 83.08 | 23.4 | 22.98
| NESC LIGHT |  | CNTRP | -13.65 | -3.95 | -47.24 | 83.62 | 11.6 | -27.07
| NESC LIGHT |  | BASERP | -14.08 | -3.79 | -48.7 | 81.7 | 11.9 | -22.12
| NESC LIGHT |  | TOPLP | -5.35 | -3.68 | -20.03 | 79.88 | 15.7 | -31.79
| NESC LIGHT |  | CNTLP | -6.23 | -3.13 | -22.99 | 74.12 | 16.3 | -12.76
| NESC LIGHT |  | BASELP | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT |  | TOPX | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT |  | CNTX | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT |  | BASEX | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT |  | BASEXY | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT |  | BASEY | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT |  | BASERY | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT |  | BASELY | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME |  | TOPP | -15.09 | -4.02 | 54.02 | 107.7 | 16.7 | 32.65
| NESC EXTREME |  | CNTP | -7.25 | -4.71 | 28.07 | 118.46 | 18.3 | 30.42
| NESC EXTREME |  | BASEP | -6.17 | -3.58 | 24.46 | 93.96 | 18.5 | 30.59
| NESC EXTREME |  | TOPRP | -15.62 | -4.31 | 55.78 | 114.26 | 16.6 | 32.79
| NESC EXTREME |  | CNTRP | -8.53 | -5.14 | -29.79 | 116.03 | 9 | -35.95
| NESC EXTREME |  | BASERP | -9.07 | -5.03 | -31.65 | 114.42 | 9.3 | -32.6
| NESC EXTREME |  | TOPLP | -3.2 | -4.78 | -12.33 | 110.87 | 11.6 | -37.86
| NESC EXTREME |  | CNTLP | -4.34 | -4.36 | -16.15 | 105.69 | 12.2 | -24.94
| NESC EXTREME |  | BASELP | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME |  | TOPX | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME |  | CNTX | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME |  | BASEX | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME |  | BASEXY | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME |  | BASEY | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME |  | BASERY | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME |  | BASELY | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME |  | TOPP | -15.96 | -5.34 | 56.64 | 152.99 | 15 | 46.1
| TEC EXTREME |  | CNTP | -7.79 | -6.03 | 29.58 | 162.05 | 16.6 | 42.34
| TEC EXTREME |  | BASEP | -6.16 | -4.91 | 24.16 | 136.77 | 17 | 43.3
| TEC EXTREME |  | TOPRP | -16.76 | -5.61 | 59.28 | 159.71 | 14.7 | 46.04
| TEC EXTREME |  | CNTRP | -9.41 | -6.95 | -32.38 | 163.81 | 6.8 | -50.26
| TEC EXTREME |  | BASERP | -10.23 | -6.87 | -35.16 | 162.57 | 7.2 | -46.76
| TEC EXTREME |  | TOPLP | -3.18 | -6.27 | -11.96 | 154.56 | 9.7 | -50.94
| TEC EXTREME |  | CNTLP | -4.88 | -5.94 | -17.7 | 150.69 | 10.6 | -37.37
| TEC EXTREME |  | BASELP | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME |  | TOPX | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME |  | CNTX | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME |  | BASEX | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME |  | BASEXY | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME |  | BASEY | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME |  | BASERY | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME |  | BASELY | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT 15 DEG |  | TOPP | -21.93 | -5.14 | 78.31 | 161.19 | 23.2 | 48.71
| NESC LIGHT 15 DEG |  | CNTP | -10.56 | -6.27 | 40.61 | 176.42 | 25 | 44.85
| NESC LIGHT 15 DEG |  | BASEP | -8.76 | -4.72 | 34.6 | 141.5 | 25.5 | 45.82
| NESC LIGHT 15 DEG |  | TOPRP | -22.83 | -5.52 | 81.24 | 170.58 | 22.9 | 48.74
| NESC LIGHT 15 DEG |  | CNTRP | -12.78 | -7.52 | -44.17 | 177.14 | 10.6 | -54.84
| NESC LIGHT 15 DEG |  | BASERP | -13.71 | -7.4 | -47.34 | 175.3 | 11.2 | -50.04
| NESC LIGHT 15 DEG |  | TOPLP | -4.57 | -6.7 | -17.23 | 166.79 | 14.5 | -56.69
| NESC LIGHT 15 DEG |  | CNTLP | -6.48 | -6.22 | -23.72 | 161.01 | 15.9 | -38.15
| NESC LIGHT 15 DEG |  | BASELP | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT 15 DEG |  | TOPX | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT 15 DEG |  | CNTX | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT 15 DEG |  | BASEX | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT 15 DEG |  | BASEXY | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT 15 DEG |  | BASEY | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT 15 DEG |  | BASERY | 0 | 0 | 0 | 0 | 0 | 0
| NESC LIGHT 15 DEG |  | BASELY | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME 15 DEG |  | TOPP | -14.47 | -6.11 | 51.9 | 176.47 | 16.5 | 52.82
| NESC EXTREME 15 DEG |  | CNTP | -7.51 | -6.66 | 28.85 | 182.89 | 17.8 | 48.88
| NESC EXTREME 15 DEG |  | BASEP | -5.57 | -5.63 | 22.36 | 159.16 | 18.1 | 48.95
| NESC EXTREME 15 DEG |  | TOPRP | -15.42 | -6.35 | 55.05 | 182.74 | 16.3 | 52.95
| NESC EXTREME 15 DEG |  | CNTRP | -7.91 | -7.76 | -27.62 | 187.54 | 8.2 | -57.13
| NESC EXTREME 15 DEG |  | BASERP | -8.89 | -7.69 | -30.93 | 186.04 | 8.7 | -53.89
| NESC EXTREME 15 DEG |  | TOPLP | -2.58 | -7.01 | -10.14 | 177.05 | 10.8 | -56.71
| NESC EXTREME 15 DEG |  | CNTLP | -4.61 | -6.67 | -16.96 | 172.01 | 11.8 | -44.14
| NESC EXTREME 15 DEG |  | BASELP | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME 15 DEG |  | TOPX | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME 15 DEG |  | CNTX | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME 15 DEG |  | BASEX | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME 15 DEG |  | BASEXY | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME 15 DEG |  | BASEY | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME 15 DEG |  | BASERY | 0 | 0 | 0 | 0 | 0 | 0
| NESC EXTREME 15 DEG |  | BASELY | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME 15 DEG |  | TOPP | -15.29 | -7.56 | 54.38 | 226.56 | 14.9 | 67.69
| TEC EXTREME 15 DEG |  | CNTP | -8.06 | -8.11 | 30.4 | 231.02 | 16.2 | 62.13
| TEC EXTREME 15 DEG |  | BASEP | -5.52 | -7.12 | 21.96 | 206.74 | 16.7 | 63.03
| TEC EXTREME 15 DEG |  | TOPRP | -16.53 | -7.78 | 58.46 | 232.9 | 14.6 | 67.61
| TEC EXTREME 15 DEG |  | CNTRP | -8.75 | -9.77 | -30.05 | 240.42 | 6 | -72.93
| TEC EXTREME 15 DEG |  | BASERP | -10.02 | -9.74 | -34.36 | 239.36 | 6.6 | -69.58
| TEC EXTREME 15 DEG |  | TOPLP | -2.53 | -8.66 | -9.66 | 225.44 | 8.8 | -71.12
| TEC EXTREME 15 DEG |  | CNTLP | -5.17 | -8.43 | -18.56 | 221.88 | 10.3 | -58.01
| TEC EXTREME 15 DEG |  | BASELP | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME 15 DEG |  | TOPX | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME 15 DEG |  | CNTX | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME 15 DEG |  | BASEX | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME 15 DEG |  | BASEXY | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME 15 DEG |  | BASEY | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME 15 DEG |  | BASERY | 0 | 0 | 0 | 0 | 0 | 0
| TEC EXTREME 15 DEG |  | BASELY | 0 | 0 | 0 | 0 | 0 | 0
Reactions At Pole Groundlines By Load Case
| Pole | Load Case |  | Long. (X) | Trans. (Y) | Vert. (Z) | Moment | Moment | Moment
| Label | Name |  | Shear | Shear | Force | About X Axis | About Y Axis | About Z Axis
|  |  |  | (kips) | (kips) | (kips) | (ft-k) | (ft-k) | (ft-k)
| PKL | NESC LIGHT |  | -4.01 | 1.44 | -0.71 | 23.83 | -72.19 | 0
| PKL | NESC EXTREME |  | -2.91 | 0.8 | -0.55 | 11.91 | -52.31 | 0
| PKL | TEC EXTREME |  | -2.61 | 1.1 | -0.55 | 17.31 | -46.91 | 0
| PKL | NESC LIGHT 15 DEG |  | -3.88 | 1.48 | -0.71 | 24.49 | -69.76 | 0
| PKL | NESC EXTREME 15 DEG |  | -2.81 | 1.55 | -0.55 | 25.51 | -50.61 | 0
| PKL | TEC EXTREME 15 DEG |  | -2.52 | 1.77 | -0.55 | 29.48 | -45.39 | 0
| PKR | NESC LIGHT |  | -4.01 | 1.45 | -0.71 | 24.03 | -72.13 | 0
| PKR | NESC EXTREME |  | -2.91 | 0.8 | -0.55 | 12 | -52.29 | 0
| PKR | TEC EXTREME |  | -2.61 | 1.1 | -0.55 | 17.41 | -46.88 | 0
| PKR | NESC LIGHT 15 DEG |  | -3.87 | 1.49 | -0.71 | 24.68 | -69.7 | 0
| PKR | NESC EXTREME 15 DEG |  | -2.81 | 1.56 | -0.54 | 25.61 | -50.57 | 0
| PKR | TEC EXTREME 15 DEG |  | -2.52 | 1.78 | -0.55 | 29.57 | -45.34 | 0
| LLF | NESC LIGHT |  | -3.14 | 1.5 | -85.65 | 23.42 | -86.18 | 1.9
| LLF | NESC EXTREME |  | -4.31 | 1.05 | -57.78 | 16.57 | -118.86 | 1.4
| LLF | TEC EXTREME |  | -5.69 | 0.96 | -61.45 | 14.72 | -166.2 | 1.8
| LLF | NESC LIGHT 15 DEG |  | -5.71 | 1.46 | -84.17 | 22.86 | -177.39 | 2.3
| LLF | NESC EXTREME 15 DEG |  | -6.44 | 1.03 | -57.01 | 16.29 | -190.25 | 1.8
| LLF | TEC EXTREME 15 DEG |  | -7.95 | 0.95 | -60.58 | 14.59 | -242.5 | 2.2
| LLB | NESC LIGHT |  | 3.74 | -0.54 | 49.36 | -11.56 | 87.87 | 1.9
| LLB | NESC EXTREME |  | 4.92 | -0.43 | 31.12 | -8.99 | 121.46 | 1.1
| LLB | TEC EXTREME |  | 6.69 | -0.32 | 33.86 | -6.79 | 171.34 | 1.1
| LLB | NESC LIGHT 15 DEG |  | 7.23 | -0.49 | 46.2 | -10.56 | 185.43 | 1.6
| LLB | NESC EXTREME 15 DEG |  | 7.51 | -0.39 | 28.89 | -8.24 | 196.05 | 0.8
| LLB | TEC EXTREME 15 DEG |  | 9.46 | -0.29 | 31.48 | -5.97 | 251.23 | 0.8
| RLF | NESC LIGHT |  | -2.7 | 1.51 | -84.21 | 23.6 | -76.86 | -0.9
| RLF | NESC EXTREME |  | -4.01 | 1.05 | -55.94 | 16.72 | -112.54 | -0.3
| RLF | TEC EXTREME |  | -5.4 | 0.97 | -58.7 | 14.98 | -159.78 | -0.2
| RLF | NESC LIGHT 15 DEG |  | -5.3 | 1.48 | -81.1 | 23.24 | -168.39 | -0.3
| RLF | NESC EXTREME 15 DEG |  | -6.17 | 1.04 | -53.72 | 16.52 | -184.2 | 0.1
| RLF | TEC EXTREME 15 DEG |  | -7.7 | 0.96 | -56.32 | 14.95 | -236.46 | 0.3
| RLB | NESC LIGHT |  | 3.58 | -0.55 | 50.89 | -11.85 | 84.61 | -2.3
| RLB | NESC EXTREME |  | 4.81 | -0.44 | 33.06 | -9.27 | 118.96 | -1.7
| RLB | TEC EXTREME |  | 6.6 | -0.34 | 36.77 | -7.23 | 169.15 | -1.9
| RLB | NESC LIGHT 15 DEG |  | 7.09 | -0.52 | 49.49 | -11.2 | 182.29 | -2.4
| RLB | NESC EXTREME 15 DEG |  | 7.42 | -0.41 | 32.33 | -8.7 | 193.68 | -1.8
| RLB | TEC EXTREME 15 DEG |  | 9.42 | -0.31 | 35.96 | -6.63 | 249.26 | -2.1
| PKRR | NESC LIGHT |  | -4.02 | 1.43 | -0.71 | 23.53 | -72.29 | 0
| PKRR | NESC EXTREME |  | -2.91 | 0.79 | -0.55 | 11.77 | -52.34 | 0
| PKRR | TEC EXTREME |  | -2.61 | 1.09 | -0.55 | 17.19 | -46.96 | 0
| PKRR | NESC LIGHT 15 DEG |  | -3.88 | 1.46 | -0.71 | 24.23 | -69.85 | 0
| PKRR | NESC EXTREME 15 DEG |  | -2.82 | 1.55 | -0.54 | 25.4 | -50.67 | 0
| PKRR | TEC EXTREME 15 DEG |  | -2.53 | 1.77 | -0.55 | 29.38 | -45.47 | 0
| RRLF | NESC LIGHT |  | 3.53 | -0.68 | 20.91 | -15.72 | 85.64 | 7.5
| RRLF | NESC EXTREME |  | 4.61 | -0.51 | 12.87 | -11.58 | 117.07 | 4.4
| RRLF | TEC EXTREME |  | 6.09 | -0.42 | 12.51 | -9.67 | 162.68 | 4.4
| RRLF | NESC LIGHT 15 DEG |  | 6.52 | -0.63 | 18.03 | -14.52 | 176.04 | 6.4
| RRLF | NESC EXTREME 15 DEG |  | 6.83 | -0.47 | 10.61 | -10.79 | 185.88 | 3.4
| RRLF | TEC EXTREME 15 DEG |  | 8.47 | -0.39 | 10.15 | -8.84 | 236.36 | 3.3
| RRLB | NESC LIGHT |  | -3.75 | 1.55 | -41.08 | 25.82 | -94.85 | 6.8
| RRLB | NESC EXTREME |  | -4.64 | 1.09 | -28.84 | 18.31 | -122.2 | 4.9
| RRLB | TEC EXTREME |  | -5.99 | 1.01 | -30.42 | 16.6 | -167.38 | 6
| RRLB | NESC LIGHT 15 DEG |  | -6.31 | 1.51 | -41.72 | 25.04 | -181.86 | 7.7
| RRLB | NESC EXTREME 15 DEG |  | -6.64 | 1.07 | -29.64 | 17.85 | -189.21 | 5.7
| RRLB | TEC EXTREME 15 DEG |  | -8.13 | 0.99 | -31.27 | 16.22 | -239.12 | 6.9
| PKLL | NESC LIGHT |  | -4 | 1.47 | -0.7 | 24.36 | -72.03 | 0
| PKLL | NESC EXTREME |  | -2.9 | 0.81 | -0.55 | 12.17 | -52.26 | 0
| PKLL | TEC EXTREME |  | -2.6 | 1.11 | -0.55 | 17.58 | -46.83 | 0
| PKLL | NESC LIGHT 15 DEG |  | -3.87 | 1.51 | -0.7 | 25 | -69.6 | 0
| PKLL | NESC EXTREME 15 DEG |  | -2.81 | 1.57 | -0.54 | 25.77 | -50.5 | 0
| PKLL | TEC EXTREME 15 DEG |  | -2.51 | 1.79 | -0.54 | 29.75 | -45.25 | 0
| LLLF | NESC LIGHT |  | 2.97 | -0.69 | 24.01 | -16.32 | 74.66 | -9.1
| LLLF | NESC EXTREME |  | 4.18 | -0.52 | 16.85 | -12.19 | 108.4 | -6.5
| LLLF | TEC EXTREME |  | 5.75 | -0.44 | 18.5 | -10.62 | 155.08 | -7.5
| LLLF | NESC LIGHT 15 DEG |  | 6.01 | -0.66 | 24.79 | -15.86 | 165.19 | -9.7
| LLLF | NESC EXTREME 15 DEG |  | 6.46 | -0.5 | 17.72 | -11.76 | 177.45 | -7.1
| LLLF | TEC EXTREME 15 DEG |  | 8.2 | -0.42 | 19.43 | -10.22 | 229.19 | -8.2
| LLLB | NESC LIGHT |  | -2.07 | 1.55 | -38.2 | 26.04 | -60.81 | -4.7
| LLLB | NESC EXTREME |  | -3.49 | 1.09 | -25.07 | 18.49 | -98.79 | -2.3
| LLLB | TEC EXTREME |  | -4.84 | 1.01 | -24.77 | 16.94 | -143.44 | -2.2
| LLLB | NESC LIGHT 15 DEG |  | -4.71 | 1.52 | -35.46 | 25.52 | -148.7 | -3.2
| LLLB | NESC EXTREME 15 DEG |  | -5.57 | 1.07 | -22.88 | 18.11 | -166.51 | -1.2
| LLLB | TEC EXTREME 15 DEG |  | -7.08 | 0.99 | -22.47 | 16.68 | -216.14 | -1
Vector Load Case Data
| Load Case |  | Dead Load | Wind Area | Safety | Wind/Ice | Trans. | Long. | Ice | Ice |  | # Point | Pole Defl | Pole Defl
| Name |  | Factor | Factor | Factor | Model | Wind Pr. | Wind Pr. | Thk. | Dens. | Temp | Loads | Check | Limit
[5 empty] | Poles |  | (psf) | (psf) | (in) | (psf) | (deg)
| NESC LIGHT |  | 1.5 | 1 | 1 | Wind on All | 22.5 | 0 | 0 | 56 | 0 | 22 | No Limit | 0
| NESC EXTREME |  | 1 | 1 | 1 | Wind on All | 26 | 0 | 0 | 56 | 0 | 22 | No Limit | 0
| TEC EXTREME |  | 1 | 1 | 1 | Wind on All | 26 | 0 | 0 | 56 | 0 | 22 | No Limit | 0
| NESC LIGHT 15 DEG |  | 1.5 | 1 | 1 | Wind on All | 22.5 | 0 | 0 | 56 | 0 | 22 | No Limit | 0
| NESC EXTREME 15 DEG |  | 1 | 1 | 1 | Wind on All | 26 | 0 | 0 | 56 | 0 | 22 | No Limit | 0
| TEC EXTREME 15 DEG |  | 1 | 1 | 1 | Wind on All | 26 | 0 | 0 | 56 | 0 | 22 | No Limit | 0